[image: image39.wmf] 

[image: image2.png]


 

[image: image3.png]3222222222202 22220208



 

General Specifications - Bimetal Dial Thermometers

CASE: Sturdy, corrosion resistant series 304 stainless steel case and bezel. Designed and constructed to provide a hermetic seal which prevents crystal fogging and damage caused by moisture to the working components.

DIAL: Anti parallax heavy gauge aluminum with white matte finish to reduce glare.Dished form with Celsius on lower inner plane and Fahrenheit on raised outer plane offers accurate indication of both scales.

 EXTERNAL RESET: A slotted-hex adjust​ment head offers screwdriver or wrench use to field calibrate the thermometer. This feature allows maximum accuracy at a selected area of temperature range. O-ring gasket prevents leakage and maintains weather tight seal. Note - use well agitated bath and accurate test thermometer when making any adjustment.

 CRYSTAL: Optically clear, strong glass, gasketed to maintain weather tight integrity. Acrylic and Lexan crystals are available as an option but not recommended for case temperature exceeding 200°F maximum (150°F maximum for plastic/acrylic lens).

.

[image: image4.png]


 

POINTER: Balanced, lightweight aluminum with matte black finish.

STEM: 304 SS welded at tip and case connector to prevent leakage. 1/4" diameter is standard, 3/8" is avail​able. Stem lengths to 72" are available as well as 316SS stem and connector assemblies.

[image: image1.png]Y




IMMERSION: For accurate temperature readings, immerse the stem a minimum of 2 inches in agitated liquid or 4 inches in moving air or gas.

OVER RANGE: Temporary over or under range of 50% of scale up to 500°F or 260°C will not affect the instrument's accuracy.

BIMETAL ELEMENT: An extremely responsive temperature sensing helix which 

has been carefully sized and tested, heat treated and aged to relieve inherent stresses and insure continued accuracy.

ACCURACY: Guaranteed to be accurate to within 1% of full scale (Grade A per ASME B40.3). Calibration is to standards traceable to the National Institute of Standards and Technology.

HERMETIC SEAL: Hermetically sealed per ASME B40.3. Guaranteed not to fog up.

DAMPENING: Bimetal element is coated with viscous silicone to minimize pointer oscillation and to improve temperature transmission for ranges from -20° to 400°F.

FILLED THERMOMETER POLICY: It is not recommended that filled instru​ments be used for continual use at operating temperatures above of 400°F(204°C) or below -100° F(-70° C}. Under no circumstances will an instrument warranty apply nor will the manufacturer assume any liability for use above these temperatures.

 Model 20 Thermometers are high-quality, economical thermometers designed for limited space and OEM applications

CASE: 304 Stainless Steel

DIAL: Anti Parallax or flat dial, heavy gauge aluminum with white matte finish.

CRYSTAL: Fully gasketed glass standard. Lexan and acrylic available.

HERMETIC SEAL: Per ASME B40.3

STEM: 304 Stainless Steel, TIG welded at tip and case connection. 1/4" diameter

standard.

DAMPENING: Helix coated with viscous silicone to minimize pointer oscillation and improve sensitivity (ranges below 500°F).

OVER RANGE: Temporary over or under range tolerance of 50% of scale up to 500°F (260°C)

 ACCURACY: Guaranteed to 1 % of full scale (Grade A per ASME B40.3 Standard) 

CONNECTION: 1/4" NPT, 304 Stainless Steel standard, other connections available. 

STEM LENGTHS: (In Inches) 2-1/2" to 24" available

' 

Stem lengths are available from 2-112" to 24". Ranges from - 100 `F (-70 C) to 1000 `F (550 V) are available. Please see page 15 for complete stem length, range and option selec​tion. Silicone fill not available on this model.
[image: image5.png]op



 


[image: image6.wmf] 


[image: image35.png]TREND instruments, inc.

A Division of WIKA Instrument Corperation



[image: image36.wmf][image: image37.png]



Back Connected Bimetal Thermometers Model 30 & 50

[image: image7.png]


 

[image: image8.png]


 

[image: image38.png]


[image: image9.png]


 

· Stainless Steel Case

· Hermetically Sealed
· External Adjustment Screw Standard
TREND Bimetal Thermometers are ideal for most rugged industrial temperature measurement applications. The hermetically-sealed case offers protection from weather and dust, and is guaranteed against fogging up. The bimetal helix is coated with a viscous silicone to minimize pointer oscillation and improve temperature transmission. 
CASE: 304 Stainless Steel

DIAL: Anti Parallax, heavy gauge aluminum with white matte finish.

EXTERNAL RESET Slotted hex adjustment

CRYSTAL: Fully gasketed glass standard. Lexan, acrylic and shatterproof available.

HERMETIC SEAL: Hermetically sealed per ASME B40.3 Standard. GUARANTEED NOT TO FOG UP
STEM: 304 Stainless Steel, TIG welded at tip and case connection. 1/4" diameter standard; 3/8" diam​eter available.

DAMPENING: Helix coated with viscous silicone to minimize pointer oscillation and improve sensitivity (ranges below 500°F).

OVER RANGE: Temporary over or under range tolerance of 50% of scale up to 500°F (250°C) ACCURACY: Guaranteed to 1% of full scale (Grade A per ASME B40.3 Standard)

CONNECTION: 1/2" NPT, 304 Stainless Steel standard, other connections and 316 Stainless Steel available.

STEM LENGTHS: (In Inches) 2-1/2, 4, 6, 9, 12, 15, 18, 24, up to 72" upon application.

OPTIONS: Silicone Fill, Custom Dials, Min-Max Pointer, Union Locknut, Union Connection and more available.

[image: image10.png]¥ |<— 3-1/4”or5-1/4"—>|

15/16"
5/16"

o

*Reset
\ 7/8" HEX



 

[image: image11.png]o \
(Stem 1/2" NPT
Length)
> 174

'S



 

Back Connected (Models 30 & 50)

[image: image12.png]


 

[image: image13.png]


 

Bottom Connected Bimetal Thermometers Model 31 & 51

· Stainless Steel Case

· Hermetically Sealed

· External Adjustment Screw Standard

TREND Model 31 and 51 Bimetal Thermometers offer the same features as the Model 30 and 50, with a fixed lower mount (bottom) connection. The hermetically-sealed case offers protection from weather and dust, and is guaranteed against fogging up. The bimetal helix is coated with a viscous silicone to minimize pointer oscillation and improve temperature trans​mission. 
[image: image14.png]


 

[image: image15.png]-1/8" —|

716"

3-1/4"

or
5-1/4°
7/8" HEX




 

CASE: 304 Stainless Steel

DIAL: Anti Parallax, heavy gauge aluminum with while matte finish.

EXTERNAL RESET Slotted hex adjustment 

CRYSTAL: Fully gasketed glass standard. Lexan, acrylic and shatterproof available.

HERMETIC SEAL: Hermetically sealed per ASME B40.3 Standard. GUARANTEED NOT TO FOG UP 

STEM: 304 Stainless Steel, TIG welded at tip and case connection. 1/4" diameter standard; 3/8" diameter available.

DAMPENING: Helix coated with viscous silicone to minimize pointer oscillation and improve sensitivity (ranges below 500°F).

OVER RANGE: Temporary over or under range toler​ance of 50% of scale up to 500°F (260°C) 

ACCURACY: Guaranteed to 1 % of full scale (Grade A per ASME B40.3 Standard)

CONNECTION: 1/2" NPT, 304 Stainless Steel standard, other connections and 316 Stainless Steel available. 

STEM LENGTHS: (In Inches) 2-112, 4, 6, 9, 12, 15, 18, 24, up to 72" upon application. 

OPTIONS: Silicone Fill, Custom Dials, Min-Max Pointer, Union Locknut, Union Connection and more available.

Bottom Connected (Models 31 & 51)


 

[image: image16.png]


 

TREND's Industrial Grade Bimetal Dial Thermometers offer performance equal to our Process-Grade thermometers, but without the reset feature and the 7​Year Warranty. They are an ideal choice where a weather-resistant, tamper​proof thermometer is needed. They are warranted for 1 year.

· Stainless Steel Case
· Hermetically Sealed
· Tamper-Proof

· [image: image17.png]SPECIFICATIONS » » * * 2222200000000 00800800ssssansas



 

CASE: 304 Stainless Steel

DIAL: Anti Parallax, heavy gauge aluminum with white matte finish.

CRYSTAL: Fully gasketed glass standard. Lexan, acrylic and shatterproof available.

HERMETIC SEAL: Per ASME B40.3

STEM: 304 Stainless Steel, TIG welded at tip and case connection. 1/4" diameter standard.

ACCURACY Guaranteed to 1 % of full scale (Grade A per ASME B40.3 Standard)

CONNECTION: 112" NPT, 304 Stainless Steel standard.

OPTIONS: Special ranges, custom dials, stems, connections and windows. 

OVER RANGE: Temporary over or under range tolerance of 50% of scale up to 500°F (260°C).
Stem lengths are available from 2-1/2" to 24". Ranges from -'100°F (-70 °C) to 1000 °F (550°C) are available. 
[image: image18.png]r‘— 3-5/16" —-‘

78" HEX

(sten
Lengty)

1/2' NPT

Back Connected Model 33



 

[image: image19.png](Stem 1/2:NPT
Length)

Back Connected Model 53



 

[image: image20.png]


 

[image: image21.png]174

Bottom Connected (Models 34 & 54)



 


[image: image22.png]


 

[image: image23.png]


 

· Dial Adjusts to Any Angle

· Stainless Steel Case

· Hermetically Sealed

· External Adjustment Screw Standard

TREND Model 32 and 52 Bimetal Thermometers offer the same features as the Model 30 and 50, with the added convenience of an all-angle swivel connection. The hermetically-sealed case offers protection from weather and dust, and is guaranteed against fog​ging up. The bimetal helix is coated with a viscous silicone to minimize pointer oscillation and improve temperature transmission. TREND Model 32 and 52 Thermometers are guaranteed for 7 years.

[image: image24.png]


 

[image: image25.png]


 

[image: image26.png]s+a11er  ——|

12 NPT
S ~—2.7/16"

(Stem
Length)

— |- 14"

Adjustable Angle (Models 32 & 52)



 

CASE: 304 Stainless Steel

DIAL: Anti Parallax, heavy gauge aluminum with a white matte finish.

EXTERNAL RESET: Slotted hex adjustment

CRYSTAL: Fully gasketed glass standard. Lexan, acrylic and shatterproof available.

HERMETIC SEAL: Hermetically sealed per ASME B40.3 Standard. GUARANTEED NOT TO FOG UP

 STEM: 304 Stainless Steel, TIG welded at tip and case connection. 1/4" diameter standard; 3/8" diameter avail​able.

DAMPENING: Helix coated with viscous silicone to minimize pointer oscillation and improve sensitivity (ranges below 500°F).

OVER RANGE: Temporary over or under range tolerance of 50% of scale up to 500°F (260°C)

ACCURACY: Guaranteed to 1 % of full scale (Grade A per ASME 840.3 Standard)

CONNECTION: 1/2" NPT, 304 Stainless Steel standard, other connections and 316 Stainless Steel available. 

STEM LENGTHS: (In Inches) 2-1/2, 4, 6, 9, 12, 15, 18, 24, up to 72" upon application.

OPTIONS: Silicone Fill, Custom Dials, Min-Max Pointer, Union Locknut, Union Connection and more available. 

JUST -RITE* ADJUSTABLE ANGLE CASE: Simple adjustment of the heavy duty stainless steel harness allows case rotation of 360° and stem variation of more than 180°. Flexible stainless steel bellows sealed at case and stem connector protects the temperature transmission mechanism and guarantees the hermetic seal.


Bimetal Thermometer Options

Adjustable Union Connection
The TREND Adjustable Union Connection allows
for the installation of a Model 32 or 52 Adjustable
Angle Thermometer without rotating the case. Ideal
for use in a confined space. See "How To Order" on
next page for this option.

Maximum or Minimum Indicating Pointer

This option allows operator to view what the highest or lowest temperature has been in the process. High vibration environments are not recommended. Please see "How To Order" on next page for this option.

[image: image27.png]TREND Bimetn

12NeT
Thread meter

5% Peied
172 NPSM)
Trvead
Adapter
Nt

i m





T-85 Thermowell Conversion Kit

I

[image: image28.png]


 

Union Lock Nut

The TREND Union Lock Nut provides a simple and inexpensive means to mount WIKA Bimetal thermometers with 112 NPT so that the dial is oriented for proper view​ing. For more information, please consult factory. To order, specify part number TA600-01 11.

This conversion kit offers an easy, inexpensive way to install a TREND
Bimetal thermometer in a glass industrial thermometer's thermowell. For
more information, please consult factory. To order, specify Part Number
TA800-0T85.

[image: image29.png]


 

I

Left. Right or Top Connection


All TREND 3" and 5" Bottom Connected thermometers are
available with the connection oriented to the left, right or top.
Please see "How to Order" on next page for this option.

Silicone Fill

All TREND 3" and 5" Process-Grade bimetal thermometers are
available with Silicone Fill, for applications where severe vibration is a factor. The silicone dampens and lubricates the internal mecha​nism, reducing oscillation and premature wear. (Maximum tempera​ture: 501500°F) Please see "How to Order" on next page


[image: image30.png]


 

[image: image31.png]


 

Not Shown
· Heavy duty 3/8" stems and 3/8" stems with 2-1/2" x 1/4" OD

sensitive portion available.

· Thermometers may be ordered with sharp tips for piercing

media to be measured.

· 316 Stainless Steel wetted parts are available.

· Paper, Aluminum and Stainless Steel tags are available

options.

· Please see these options on Table 8 of "How To Order" on

next page.

Other options are available. Please consult factory.

[image: image32.png]Duct Flange
Part # TA800-0020




 

	Tags and Certificates


	Part #
	DESCRIPTION

	1411004
	Stainless Steel Tag

	776
	Certificate of Calibration

	413
	Factory Certificate of Accuracy



How to Order Bimetal Thermometers

[image: image33.png]Specify Complete Model Number from the following tables:

KEY MODEL NUMBER 30 060 A 0 01G 4 XX
TABLE 1:  BASIC MODEL——

TABLE STEM LENGTH

TABLE3:  DIAL TYPE (LOGO)

TABLE 4:  SCALE TYPE (F, C ORF & C)

TABLE5: RANGE
TABLE6: CRYSTAL MATERIAL
TABLE7:  CONNECTION
TABLES: OPTIONS (3' & 5" ONLY)




 


Proceed to Table 4, top of next column.

	Table 4 - Scale Type

	KEY
	DESCRIPTION

	0
	Dual Scale Fahrenheit and Celsius

	1
	Single Scale Celsius Only

	2
	Single Scale Fahrenheit Only



	Table 6 - Crystal Material

	KEY
	DESCRIPTION

	A
	Acrylic Plastic (Standard w/Silicone Fill)

	G
	Plain Glass (Standard)

	L
	Lexan®

	S
	Shatterproof Safety Glass (3" & 5" Dials Only)


	Table 7 - Connection

	0
	Plain (Unthreaded)

	1
	1/8" NPT

	2
	1/4" NPT (Standard on Model 20)

	3
	3/8"NPT

	4
	1/2" NPT (Standard on 3" & 5" Models)

	5
	1/2" BSP (Models 30 & 50 lnly)

	7
	1/2" NPT Adjustable Union (Models 32 & 52)


	Table 8 - Options (3" & 5" Models)

	Blank
	None

	SF*
	Silicone Filled - (Models 30, 31, 32, 50, 51, 52 Only)

	MM
	Min/Max Pointer (Models 30 and 50 Only)

	LS
	Left Side Connection (Models 31, 34, 51, 54 Only)

	RS
	Right Side Connection (Models 31, 34, 51, 54 Only)

	TS
	Top Connection (Models 31, 34, 51, 54 Only)

	HD
	3/8" Heavy Duty Stem with 2-1/2" x 1/4" O.D. 
Sensitive Tip

	HA
	3/8" Heavy Duty Stem Entire Length

	ST
	Sharp Tip

	SS
	316 Stainless Steel Wetted Parts

	DF
	Dry w/plug

	*Requires Acrylic lens


	
	Dual Scale
	Single Scale

	Key
	°F Range
	Figure

Int. Div.
	Figure
"C Range Int. Div.
	'F Range
	'C Range

	01
	-100/150
	20
	2
	-70/70
	10
	1
	-100/150
	-70/70

	02
	-40/120
	20
	2
	-40/50
	10
	1
	-40/120
	-50/50

	14
	-20/120
	20
	2
	-30/50
	10
	1
	-20/120
	NA

	19
	-40/160
	20
	2
	-40/70
	10
	1
	-40/160
	NA

	*23
	0/100
	10
	1
	-20/40
	5
	1/2
	NA
	NA

	*03
	25/125
	10
	1
	-5/50
	5
	1/2
	NA
	NA

	*15
	30/130
	10
	1
	0155
	5
	1/2
	30/130
	NA

	04
	0/140
	10
	1
	-20/60
	5
	1/2
	0/140
	NA

	05
	0/200
	20
	2
	-15/90
	10
	1
	0/200
	0/100

	06
	01250
	20
	2
	-20/120
	10
	1
	0/250
	-20/120

	07
	20/240
	20
	2
	-5/115
	10
	1
	20/240
	NA

	08
	50/300
	20
	2
	10/150
	10
	1'
	50/300
	0/150

	09
	50/400
	50
	5
	10/200
	20
	2
	50/400
	0/200

	10
	50/500
	50
	5
	10/260
	20
	2
	50/500
	NA

	16
	50/550
	50
	5
	10/290
	20
	2
	50/550
	0/250

	17
	0/600
	100
	10
	-20/315
	50
	5
	0/600
	NA

	11
	150/750
	100
	10
	65/400
	50
	5
	150/750
	0/300

	18
	100/800
	100
	10
	40/425
	50
	5
	100/800
	0/450

	12
	200/1000
	100
	10
	100/450
	50
	5
	 200/1000
	100/550


*Not available with 2-1/2" stem on Models 31, 32, 34, 57, 52, 54

[image: image34.png]


 



Tamper-Proof Bimetal Thermometers Models 33, 34, 53 & 54








Adjustable Angle Bimetal Thermometers Model 32 & 52





Stainless Steel Case


Hermetically Sealed


Tamper-Proof





SPECIFICATIONS





SPECIFICATIONS





SPECIFICATIONS





SPECIFICATIONS





Table 2 - Stem Length�
�
KEY�
DESCRIPTION�
�
xx.x�
Length in inches with one decimal place�
�









Table 3 - Dial Type�
�
KEY�
DESCRIPTION�
�
A�
TREND Standard�
�
X�
Special�
�






Table 1 - Model


�
�
KEY�
DESCRIPTION�
�
20�
2" Back Connected (No Reset)�
�
30�
3" Back Connected (With Reset)�
�
31�
3" Bottom Connected (With Reset)�
�
32�
3" Adjustable Angle (With Reset)�
�
33�
3" Back Connected (No Reset)�
�
34�
3" Bottom Connected (No Reset)�
�
50�
5" Back Connected (With Reset)�
�
51�
5" Bottom Connected (With Reset)�
�
52�
5" Adjustable Angle (With Reset)�
�
53�
5" Back Connected (No Reset)�
�
54�
5" Bottom Connected (No Reset)�
�






Table 5 - Range (See Bottom of Page)





�





2” Bimetal Dial Thermometers – Model 20





Table 1 - Model


�
�
KEY�
DESCRIPTION�
�
20�
2" Back Connected (No Reset)�
�
30�
3" Back Connected (With Reset)�
�
31�
3" Bottom Connected (With Reset)�
�
32�
3" Adjustable Angle (With Reset)�
�
33�
3" Back Connected (No Reset)�
�
34�
3" Bottom Connected (No Reset)�
�
50�
5" Back Connected (With Reset)�
�
51�
5" Bottom Connected (With Reset)�
�
52�
5" Adjustable Angle (With Reset)�
�
53�
5" Back Connected (No Reset)�
�
54�
5" Bottom Connected (No Reset)�
�






Table 2 - Stem Length�
�
KEY�
DESCRIPTION�
�
xx.x�
Length in inches with one decimal place�
�






Table 3 - Dial Type�
�
KEY�
DESCRIPTION�
�
A�
TREND Standard�
�
X�
Special�
�






Table 5 - Range








[image: image35.png] Page 6

_1157881650.doc
[image: image1.png]e
1/4°

\ 174" NPT

Stem Length
a3 Specfied

-« 1








